## Instructions
Busbar Size Calculation Workbook
IEC & NEC dual-standard rectangular busbar sizing, short-circuit withstand check
PURPOSE
This workbook sizes rectangular copper or aluminum busbars for a given continuous load current, recommends the nearest standard busbar cross-section, and checks the short-circuit thermal withstand capability of the selected size. Separate calculation tabs are provided for IEC (metric, mm/A per mm²) and NEC/US practice (imperial, in/A per in²).
HOW TO USE
1. Go to the "IEC Sizing" tab (metric) or the "NEC Sizing" tab (imperial) depending on the standard you design to.
2. Fill in the blue input cells only: load current, material, mounting condition, ambient temperature, number of parallel bars, conductor finish, run length and system voltage.
3. The sheet looks up base current density, correction factors, and the nearest standard busbar size automatically from the "Reference Tables" tab.
4. Review the recommended busbar size, utilization, estimated temperature rise, resistance, voltage drop and weight in the results block.
5. Open the "Short-Circuit Check" tab, confirm or override the busbar size (auto-linked), enter the prospective fault current and clearing time, and confirm the PASS/WARN/FAIL result.
6. Blue cells = inputs you may edit. Yellow-filled cells = key assumptions/lookup values, editable if your project data differs from the reference table. Black text = live formulas - do not overwrite.
LEGEND
|  | Blue text on yellow fill | User input cell - edit freely
|  | Navy text on light-blue fill | Section header - do not edit
|  | Black text, white fill | Live formula - recalculates automatically
|  | Green fill | PASS - within limits
|  | Amber fill | WARNING - close to limit, review
|  | Red fill | FAIL - exceeds limit, re-size busbar
STANDARDS & ENGINEERING BASIS
IEC 61439-1/2 - low-voltage switchgear and controlgear assemblies (temperature-rise and busbar practice)
IEC 60943 - guidance for the calculation of thermally permissible short-circuit current, taking into account non-adiabatic heating effects (basis for the k-factor method used here)
IEC 60865-1 - short-circuit currents - calculation of effects (thermal and mechanical)
UL 508A / NEMA industry practice - typical current-density based approach used for US switchboard and panel busbar preliminary sizing
IMPORTANT DISCLAIMER
Current-density values, correction factors and short-circuit k-factors used in this workbook are general engineering estimates compiled from common industry busbar design practice and the standards listed above. They are NOT reproduced from a single codified table and can vary with manufacturer, plating, joint design, enclosure ventilation and altitude. This workbook is intended for preliminary sizing only. Final busbar selection must be verified against the busbar manufacturer's tested ampacity and short-circuit withstand data, and against the applicable local code and the engineer of record's review.

## IEC Sizing
Busbar Sizing Calculator - IEC (Metric)
Enter blue input cells only - results and recommended size calculate automatically
1. INPUTS
Load Current, I (A) | 1000
Busbar Material | Copper
Mounting Condition | Enclosure - Natural Ventilation
Ambient Temperature (C) | 35
Bars per Phase, N | 2
Conductor Finish | Bare (unplated)
Rated Temperature Rise, base density (K) | 65
Max Permissible Hot-Spot Temperature (C) | 90
Busbar Run Length (m) | 3
System Voltage, line-to-line (V) | 415
Load Power Factor | 0.85
2. LOOKUP FACTORS (from Reference Tables)
Base Current Density (A/mm2) | 1.4
Ambient Temp Correction Factor | 1
Grouping Factor (per bar) | 0.9
Finish Correction Factor | 1
Effective Current Density (A/mm2) | 1.4
3. REQUIRED CROSS-SECTION & RECOMMENDED SIZE
Required Total Cross-Section (mm2) | 714.2857
Required Area per Bar (mm2) | 396.8254
Recommended Width (mm) | 40
Recommended Thickness (mm) | 10
Recommended Area per Bar, actual (mm2) | 400
If required area exceeds the largest standard single bar, increase bars per phase (N) above.
4. RESULTS - CAPACITY, TEMPERATURE, RESISTANCE & WEIGHT
Selected Busbar Size (W x T mm) | 40 x 10 mm
Total Bars (all phases shown = per phase) | 2
Actual Total Cross-Section, N bars (mm2) | 800
Actual Current Capacity (A) | 1008
Utilization (Load / Capacity) | 99.21%
Estimated Temperature Rise (K) | 63.9723
Estimated Hot-Spot Temperature (C) | 98.9723
Thermal Status | FAIL - exceeds max hot-spot temp
DC Resistance @20C (micro-ohm/m, per bar) | 43
AC/DC Skin-Effect Factor | 1.03
AC Resistance @20C (micro-ohm/m, N bars) | 22.145
Estimated Voltage Drop (V, 3-phase) | 0.097808
Voltage Drop (%) | 0.02357%
Weight per Bar (kg/m) | 3.584
Total Busbar Weight, run length x N bars (kg) | 21.504
Voltage drop uses a simplified resistive approximation (I x R x cos(phi)) and excludes busbar reactance -
for long runs or high-frequency-sensitive applications, verify with manufacturer reactance data.
Temperature rise is scaled from the assumed Rated Temperature Rise by (Utilization)^2 - a standard I2R approximation, not a full IEC 60890 thermal model.

## NEC Sizing
Busbar Sizing Calculator - NEC / US Practice (Imperial)
Enter blue input cells only - results and recommended size calculate automatically
1. INPUTS
Load Current, I (A) | 1000
Busbar Material | Copper
Mounting Condition | Enclosure - Natural Ventilation
Ambient Temperature (F) | 95
Bars per Phase, N | 2
Conductor Finish | Bare (unplated)
Rated Temperature Rise, base density (F) | 117
Max Permissible Hot-Spot Temperature (F) | 194
Busbar Run Length (ft) | 10
System Voltage, line-to-line (V) | 480
Load Power Factor | 0.85
Ambient/rise/hot-spot temperatures on this tab are entered directly in degrees F (e.g. 95F ambient = 35C).
2. LOOKUP FACTORS (from Reference Tables)
Base Current Density (A/in2) | 903.224
Ambient Temp Correction Factor | 1
Grouping Factor (per bar) | 0.9
Finish Correction Factor | 1
Effective Current Density (A/in2) | 903.224
3. REQUIRED CROSS-SECTION & RECOMMENDED SIZE
Required Total Cross-Section (in2) | 1.1071
Required Area per Bar (in2) | 0.61508
Recommended Width (in) | 0.375
Recommended Thickness (in) | 2
Recommended Area per Bar, actual (in2) | 0.75
If required area exceeds the largest standard single bar, increase bars per phase (N) above.
4. RESULTS - CAPACITY, TEMPERATURE, RESISTANCE & WEIGHT
Selected Busbar Size (W x T in) | 0.375 x 2 in
Total Bars per Phase | 2
Actual Total Cross-Section, N bars (in2) | 1.5
Actual Current Capacity (A) | 1219.3524
Utilization (Load / Capacity) | 82.01%
Estimated Temperature Rise (F) | 78.6914
Estimated Hot-Spot Temperature (F) | 173.6914
Thermal Status | PASS
DC Resistance @68F (micro-ohm/ft, per bar) | 10.8346
AC/DC Skin-Effect Factor | 1.03
AC Resistance @68F (micro-ohm/ft, N bars) | 5.5798
Estimated Voltage Drop (V, 3-phase) | 0.082149
Voltage Drop (%) | 0.01711%
Weight per Bar (lb/ft) | 2.9133
Total Busbar Weight, run length x N bars (lb) | 58.266
This tab follows general US/NEMA industry current-density practice for preliminary busbar sizing (see Instructions tab).
NEC itself does not publish a busbar ampacity formula; for UL-listed switchboards, verify final size against UL 508A / manufacturer-tested ampacity tables.
Voltage drop uses a simplified resistive approximation and excludes busbar reactance.

## Short-Circuit Check
Busbar Short-Circuit Thermal Withstand Check
Adiabatic (k-factor) method per IEC 60943 - verifies the sized busbar against a prospective fault current
1. SELECTED BUSBAR (auto-linked from IEC Sizing tab, or override)
Source Standard for Busbar Size | IEC Sizing
Busbar Material | Copper
Area per Bar, mm2 (auto-linked - to enter manually, set Source above to "Manual Entry" and type a value directly over this formula) | 400
Bars per Phase, N (auto, or override) | 2
Total Cross-Section, N bars (mm2) | 800
2. FAULT CURRENT INPUTS
Prospective Symmetrical Fault Current, Ik (kA rms) | 40
Protective Device Clearing Time, t (s) | 1
Adiabatic k-factor Basis | 143
3. WITHSTAND CHECK
1-Second Thermal Withstand Current, Ith(1s) (kA) | 114.4
Withstand Current at Clearing Time t, Ith(t) (kA) | 114.4
Margin (Withstand / Prospective Fault Current) | 2.86
Withstand Status | PASS
Minimum Cross-Section Required for this Fault (mm2, all bars) | 279.7203
NOTES
This is a thermal (I2t / adiabatic) withstand check only. It does not evaluate electrodynamic (mechanical) forces between
bars or at supports under fault current - for a full mechanical force and peak making current assessment, use a dedicated
busbar protection/short-circuit force calculator.
The k-factor is a general engineering estimate for an assumed initial-to-final temperature rise (see Reference Tables note) -
confirm against the actual initial operating temperature and insulation/joint class of your installation.

## Reference Tables
Reference Tables
Lookup data used by the IEC, NEC and Short-Circuit Check tabs - edit only if your project data differs
TABLE 1 - Standard Busbar Sizes (IEC, mm)
Width (mm) | Thickness (mm) | Area (mm2)
15 | 3 | 45
20 | 3 | 60
25 | 3 | 75
30 | 3 | 90
20 | 5 | 100
25 | 5 | 125
30 | 5 | 150
40 | 5 | 200
50 | 5 | 250
60 | 5 | 300
40 | 10 | 400
50 | 10 | 500
60 | 10 | 600
63 | 10 | 630
80 | 10 | 800
100 | 10 | 1000
120 | 10 | 1200
125 | 10 | 1250
160 | 10 | 1600
200 | 10 | 2000
TABLE 2 - Standard Busbar Sizes (NEC/US, inches)
Width (in) | Thickness (in) | Area (in2)
0.25 | 1 | 0.25
0.25 | 1.5 | 0.375
0.25 | 2 | 0.5
0.375 | 2 | 0.75
0.25 | 4 | 1
0.375 | 3 | 1.125
0.375 | 4 | 1.5
0.375 | 5 | 1.875
0.5 | 4 | 2
0.375 | 6 | 2.25
0.5 | 5 | 2.5
0.5 | 6 | 3
0.5 | 8 | 4
0.5 | 10 | 5
0.75 | 8 | 6
0.75 | 10 | 7.5
0.75 | 12 | 9
1 | 10 | 10
1 | 12 | 12
TABLE 3 - Base Continuous Current Density (IEC, A/mm2)
Material | Mounting Condition | Density (A/mm2)
Copper | Enclosure - Natural Ventilation | 1.4
Copper | Enclosure - Forced Ventilation | 1.7
Copper | Free Air | 2
Aluminum | Enclosure - Natural Ventilation | 1.05
Aluminum | Enclosure - Forced Ventilation | 1.3
Aluminum | Free Air | 1.55
TABLE 4 - Base Continuous Current Density (NEC/US, A/in2)
Material | Mounting Condition | Density (A/in2)
Copper | Enclosure - Natural Ventilation | 903.224
Copper | Enclosure - Forced Ventilation | 1096.772
Copper | Free Air | 1290.32
Aluminum | Enclosure - Natural Ventilation | 677.418
Aluminum | Enclosure - Forced Ventilation | 838.708
Aluminum | Free Air | 999.998
TABLE 5 - Ambient Temperature Correction Factor (base 35C)
Ambient Temp (C) | Factor
20 | 1.1
25 | 1.05
30 | 1.02
35 | 1
40 | 0.94
45 | 0.87
50 | 0.79
55 | 0.71
TABLE 6 - Grouping Factor, Parallel Bars per Phase (per-bar multiplier)
Bars per Phase (N) | Factor
1 | 1
2 | 0.9
3 | 0.8
4 | 0.72
TABLE 7 - Conductor Finish / Plating Correction Factor
Finish | Factor
Bare (unplated) | 1
Tin-Plated | 1.05
Silver-Plated | 1.1
Painted (matte black) | 1.15
TABLE 8 - AC Skin-Effect Resistance Factor (vs DC), by bar area
Area up to (mm2) | AC/DC Factor
300 | 1
600 | 1.03
1000 | 1.08
1600 | 1.15
999999 | 1.25
TABLE 9 - Material Properties
Material | Resistivity @20C (ohm.mm2/m) | Density (kg/m3) | SC k-factor 1s (A.s^0.5/mm2)
Copper | 0.0172 | 8960 | 143
Aluminum | 0.0282 | 2700 | 93
Note: current-density, correction-factor and k-factor values above are general engineering estimates for preliminary sizing (see Instructions tab disclaimer). Adjust to match manufacturer or project-specific data where available. k-factor corresponds approximately to a 20C to 250C (copper, bare) / 20C to 200C (aluminum) adiabatic temperature rise, per IEC 60943 typical values.