## Lux Calculator
IEC Lighting Lux Level Estimation Tool
Estimate required lux level and number of light fixtures using the IEC/EN 12464-1 lumen method
1. Room & Task Details
Room Type (select from list) | Office - General
Room Length (m) | 6 | m
Room Width (m) | 4 | m
Room Height / Mounting Height (m) | 3 | m
Room Area (calculated) | 24 | m²
2. Recommended Illuminance (IEC / EN 12464-1)
Recommended Lux Level (auto-lookup, editable if needed) | 500 | lux (lm/m²)
3. Luminaire & Calculation Factors
Luminous Flux per Fixture (lumens) | 4000 | lm
Utilization Factor (UF / CU) | 0.6 | 0-1
Maintenance Factor (MF / LLF) | 0.8 | 0-1
4. Results
Total Lumens Required | 15000 | lm
Number of Fixtures Required | 7 | fixtures
Actual Achieved Lux (with fixtures above) | 560 | lux
Lumen Method Formula: N = (E x A) / (F x UF x MF) N = Number of fixtures ¦ E = Required lux (lm/m²) ¦ A = Area (m²) F = Lumens per fixture ¦ UF = Utilization Factor ¦ MF = Maintenance Factor

## Reference
IEC / EN 12464-1 Recommended Illuminance Reference Table
Room / Task Type | Lux (lm/m²) | Notes
Corridor / Circulation Area | 100 | Low-traffic passage areas
Stairs | 150 | Safety-critical, avoid shadows
Storage / Warehouse (bulk) | 100 | General storage, low detail work
Storage / Warehouse (picking) | 200 | Areas with reading of labels
Parking Area (covered) | 75 | Vehicle circulation
Reception / Lobby | 200 | Includes desk task area
Office - General | 500 | EN 12464-1 standard office task
Office - Computer Work | 300 | Screen-based tasks, reduced glare
Conference / Meeting Room | 500 | Presentation & reading tasks
Classroom | 300 | General teaching space
Drawing / Technical Office | 750 | Detailed drafting work
Control Room | 500 | Panel monitoring
Laboratory | 500 | General lab bench work
Industrial - Rough Work | 200 | Rough machining, assembly
Industrial - Medium Work | 300 | Medium precision assembly
Industrial - Fine Work | 750 | Fine assembly, inspection
Industrial - Very Fine Work | 1000 | Precision instrument work
Electrical Switchgear Room | 200 | Equipment rooms
Kitchen (Commercial) | 500 | Food preparation areas
Retail - General Sales Area | 300 | Shop floor
Retail - Till / Checkout | 500 | Cashier point
Hospital - Examination Room | 500 | Medical examination
Hospital - Operating Theatre | 1000 | Surgical task area
Residential - Living Room | 150 | General living area
Source: IEC 60364-3 guidance & EN 12464-1 indicative illuminance values. Verify against the latest standard edition for compliance-critical designs.