## Instructions
MCC Panel Design & Sizing Calculator
This workbook accompanies the 'MCC Panel Design Guide (IEC Standards)'.
It provides working calculators for incomer sizing, motor feeder sizing, busbar sizing,
and a cost estimation BOM, built on IEC 60947, IEC 61439-1/2 and IEC 60364-5-52 principles.
How to use this workbook:
1. Go to 'Incomer & Busbar' - enter total connected load, voltage, PF and diversity factor.
2. Go to 'Motor Feeder Sizing' - enter each motor's nameplate data in the blue input cells.
3. Check 'Cable Ampacity Ref' for the reference table used by the lookup formulas.
4. Go to 'Cost Estimation (BOM)' - enter quantities and unit rates for a budgetary cost.
Colour code:
Blue text = input cell (edit these)
Black text = calculated (formula - do not overwrite)
Yellow fill = key assumption to review before finalising
IMPORTANT - Engineering Disclaimer:
This spreadsheet provides preliminary, budgetary sizing only. It is not a substitute for
a detailed engineering study, protection coordination (discrimination) study, arc-flash
assessment, or short-circuit withstand verification. All final MCC designs must be
reviewed and certified by a licensed electrical engineer and checked against the project's
governing standard (IEC 61439-1/2, local wiring regulations, and utility requirements)
before manufacture, energisation, or use.

## Incomer & Busbar
Incomer & Busbar Sizing Calculator
INPUTS
Total connected load | 350 | kW | Sum of all motor and load nameplate ratings
System voltage (line-line) | 415 | V | Typically 400/415V (IEC) 3-phase
Average power factor | 0.85 | - | Assumed system PF after correction
Average efficiency | 0.92 | - | Assumed average motor/load efficiency
Diversity / demand factor | 0.8 | - | IEC 61439 Annex D typical 0.7-0.9 for MCC
Ambient design temperature | 40 | deg C | IEC 60947 reference temp is 40 deg C
Busbar current density (Cu, air-insulated) | 1.6 | A/mm2 | Typical 1.2-1.6 A/mm2 for enclosed Cu busbar
CALCULATED RESULTS
Full load current (3-phase) | 622.6623 | A
Design (diversified) current, Id | 498.1298 | A
Recommended incomer breaker (ACB/MCCB) rating | 630 | A (standard frame)
Required busbar cross-section (per phase) | 12.4532 | mm2
Note: Breaker rating is picked from the standard IEC 60947-2 frame steps above the 1.25x design current. Verify short-circuit withstand (Icu/Ics) and discrimination separately.
Busbar cross-section must be split across the number of parallel bars actually used and rounded up to the next standard busbar size (see manufacturer tables).

## Motor Feeder Sizing
Motor Feeder Sizing Calculator (per IEC 60947-4-1)
Motor Tag | Rated Power (kW) | Voltage (V) | Efficiency | Power Factor | Service Factor | FLC (A) | Starting Method | Cable Size (mm2) | Contactor Rating (A) | Overload Min (A) | Overload Max (A) | MCCB / MPCB Rating (A)
M-101 Cooling Water Pump | 37 | 415 | 0.92 | 0.86 | 1.15 | 65.0589 | DOL | 10 | 80 | 68.3118 | 78.0707 | 100
M-102 Compressor | 90 | 415 | 0.94 | 0.87 | 1.15 | 153.1041 | Star-Delta | 50 | 185 | 160.7593 | 183.7249 | 250
M-103 Conveyor Drive | 15 | 415 | 0.9 | 0.83 | 1.15 | 27.9359 | DOL | 2.5 | 38 | 29.3326 | 33.523 | 50
M-104 Fan | 22 | 415 | 0.91 | 0.85 | 1.15 | 39.5689 | VFD | 4 | 60 | 41.5473 | 47.4826 | 44
FLC = P(kW)x1000 / (SQRT3 x V x Eff x PF). Overload band shown is typical 105-120% FLC (Class 10/20); confirm against the specific overload relay's trip class and motor's service factor.
MCCB/MPCB values assume standard DOL/Star-Delta motor protection multipliers; VFD-fed motors use an input-side breaker sized off the drive's rated input current, not the motor FLC alone - always check the VFD manufacturer's datasheet.

## Cable Ampacity Ref
Cable Ampacity Reference (IEC 60364-5-52, Cu, PVC/XLPE, single circuit in air, 30 deg C ambient)
Cable Size (mm2) | Approx. Ampacity (A) | Typical Use | Notes
1.5 | 19.5 | Control wiring, indication circuits | Min practical power size 2.5mm2
2.5 | 27 | Small loads, lighting
4 | 36 | Small motors up to approx 5.5kW
6 | 46 | Motors up to approx 7.5kW
10 | 63 | Motors up to approx 15kW
16 | 85 | Motors up to approx 22kW
25 | 110 | Motors up to approx 37kW
35 | 137 | Motors up to approx 45kW
50 | 167 | Motors up to approx 55-75kW
70 | 213 | Motors up to approx 90kW
95 | 258 | Motors up to approx 110kW
120 | 299 | Motors up to approx 132kW
150 | 344 | Motors up to approx 160kW
185 | 392 | Motors up to approx 200kW
240 | 461 | Feeders / large motors
300 | 530 | Main feeders
Values are indicative, derated for 30 deg C ambient, single circuit in free air, PVC/XLPE insulation. Always verify against IEC 60364-5-52 Tables B.52.2-B.52.10 with the project's actual installation method, grouping and ambient/derating factors.

## Cost Estimation (BOM)
MCC Panel Budgetary Cost Estimation (BOM)
Item / Component | Qty | Unit Rate | Currency | Total
Enclosure (form 3b/4, IP54, powder-coated), per vertical section | 4 | 1200 | USD | 4800
Main incomer ACB/MCCB (per Sheet 2 sizing) + accessories | 1 | 3500 | USD | 3500
Motor feeder MCCB/MPCB | 8 | 220 | USD | 1760
Contactor + overload relay set | 8 | 180 | USD | 1440
Busbar system (Cu, TPN, per sizing above) | 1 | 2800 | USD | 2800
Control transformer + protection | 1 | 350 | USD | 350
Metering (ammeter/voltmeter/CTs) per section | 4 | 260 | USD | 1040
Indication lamps, selector switches, push buttons | 8 | 25 | USD | 200
PLC/RTU I/O modules (if SCADA integrated) | 1 | 4500 | USD | 4500
Internal wiring, ferrules, terminals, trunking | 1 | 1500 | USD | 1500
Engineering, drawings, FAT documentation | 1 | 3000 | USD | 3000
Factory Acceptance Test (FAT) | 1 | 1200 | USD | 1200
Transportation & insurance | 1 | 900 | USD | 900
Installation & commissioning (site) | 1 | 4000 | USD | 4000
Subtotal |  |  |  | 30990
Contingency (10%) | 1 | 3099 | USD | 3099
GRAND TOTAL (budgetary) |  |  |  | 34089
Unit rates are placeholders - replace with actual vendor quotations. This BOM excludes site civil works, cable trays/ducting, and local taxes/duties unless added as separate line items.