## Calculator
Street Lighting Voltage Drop Calculator
Enter values in blue cells only. Results update automatically.
1. SYSTEM & SUPPLY
System Voltage (V) | 230
Phase Type | Single Phase
Power Factor of Lamp/Ballast | 0.9
Max. Permissible Voltage Drop (%) | 3
2. LIGHTING LOAD
Wattage per Lamp / Fixture (W) | 150
Number of Lamps / Poles on this Circuit | 20
Spacing Between Poles (m) | 30
Distance: Panel/Source to First Pole (m) | 15
3. CABLE
Conductor Material | Copper
Cable Cross-Section (mm²) | 4
Cable Resistance (Ω/km) | 4.95
4. RESULTS
Current per Lamp (A) | 0.72464
Total Circuit Current (A) | 14.4928
Multiplying Factor (2 for 1-ph, √3 for 3-ph) | 2
Cumulative Cable Moment (A·m) | 4782.6087
Total Voltage Drop (V) | 47.3478
Total Voltage Drop (%) | 20.59%
Voltage at Last Pole (V) | 182.6522
Result | FAIL
Notes
• This tool uses the standard 'moment method' for equally spaced street lighting loads (2 x I x R x moment / 1000).
• Typical design limit for street lighting circuits is 3% voltage drop end-to-end (some standards allow up to 5%).
• For 3-phase balanced circuits, current per lamp is still calculated line-to-neutral (single-phase load per pole).
• Cable resistance values (Ω/km) are approximate at normal operating temperature — see 'Cable Data' sheet.
• For unequal pole spacing or mixed loads, calculate voltage drop pole-by-pole using the same R and I x d x 2(or √3)/1000 logic.

## Cable Data
Cable Resistance Reference Table
Material | Size (mm²) | Resistance (Ω/km)
Copper | 1.5 | 13.3
Copper | 2.5 | 7.98
Copper | 4 | 4.95
Copper | 6 | 3.3
Copper | 10 | 1.91
Copper | 16 | 1.21
Copper | 25 | 0.78
Copper | 35 | 0.554
Copper | 50 | 0.386
Copper | 70 | 0.272
Copper | 95 | 0.206
Copper | 120 | 0.161
Aluminum | 1.5 | 22
Aluminum | 2.5 | 13.3
Aluminum | 4 | 8.24
Aluminum | 6 | 5.49
Aluminum | 10 | 3.08
Aluminum | 16 | 1.91
Aluminum | 25 | 1.2
Aluminum | 35 | 0.868
Aluminum | 50 | 0.641
Aluminum | 70 | 0.443
Aluminum | 95 | 0.32
Aluminum | 120 | 0.253
Values are typical approximations for PVC-insulated copper/aluminum conductors at normal operating temperature. Replace with manufacturer datasheet values for detailed design.